|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Essential Safety Measures (ESM) Routine Service – 191 Wellington Rd Seawinds Nursery**  (BCA Class 6 building)  *The Annual Essential Safety Measures Report (AESMR) SF-21, is due within a month of the pre 1994 building anniversary:* ***13th June*** *2009* | | | | |
| **Safety Measure**  *Building Regs 2018* | | **ESM Form** | **Frequency of test or inspection** | **Who is responsible?** |
|  | Part 2 **- Means of Egress** | | | |
| Paths of travel to exits | | SF-28 | Every 3 months   * to ensure no obstructions or alterations | Site OHS Rep |
| Discharge from exits (including paths of travel from open spaces to the public roads to which they are connected) | | Every 3 months   * to ensure no obstructions or alterations |
| Exits (including ramps, stair treads, handrail) | | Every 3 months  to ensure no obstructions or alterations |
| Doors in a required exit – closing, opening & latching | | Every 3 months   * to ensure doors are intact, operational and fitted with conforming hardware |
|  | Part 5 **- Fire Fighting Services & Equipment** | | | |
| Portable fire extinguishers & fire blanket | | SF-25 | Every 6 months – maintenance tag & label | Portland Aluminium |
|  | Part 7 **- Automatic Fire Detection & Alarms** | | | |
| Smoke alarms | | SF-75 | Monthly - test smoke alarm battery | Site OHS Rep |
| Annual   * clean / vacuum * replace 9-volt smoke alarm batteries   Every 10 years   * replace all smoke alarm units | External contractor |